## Dispositivos
Tipo | Tamanho | Comando | Variavel | TT301 | LD301 | FY301 | DT301
ENUMERATED | 1 | 150 | response_code
BIT_ENUMERATED | 1 | 151 | device_status
BIT_ENUMERATED | 1 | 152 | comm_status
ENUMERATED | 1 | 153 | manufacturer_id
ENUMERATED | 1 | 154 | device_type
UNSIGNED | 1 | 155 | request_preambles
UNSIGNED | 1 | 156 | universal_revision
UNSIGNED | 1 | 157 | transmitter_revision
UNSIGNED | 1 | 158 | software_revision
UNSIGNED | 1 | 159 | hardware_revision
BIT_ENUMERATED | 1 | 160 | device_flags
UNSIGNED | 3 | 161 | device_id
UNSIGNED | 1 | 162 | polling_address
PACKED_ASCII | 8 | 163 | tag | TT301 | LD301 | FY301 | DT301
PACKED_ASCII | 32 | 164 | message | Medidor de Temperatura | Medidor de Pressao | Posicionador de Valvula | Medidor de Densidade
PACKED_ASCII | 16 | 165 | descriptor
DATE | 3 | 166 | date
ENUMERATED | 1 | 167 | write_protect
ENUMERATED | 1 | 168 | private_label_distributor
UNSIGNED | 3 | 169 | final_assembly_number
ENUMERATED | 1 | 171 | physical_signaling_code
ENUMERATED | 1 | 2025 | units_code
ENUMERATED | 1 | 2026 | transfer_function_code
ENUMERATED | 1 | 2027 | alarm_selection_code
ENUMERATED | 1 | 2028 | material_code
ENUMERATED | 1 | 2029 | unique_device_type_code
ENUMERATED | 1 | 2030 | write_protect_code
ENUMERATED | 1 | 2031 | company_identification_code
ENUMERATED | 1 | 2032 | burst_mode_control_code
ENUMERATED | 1 | 2033 | physical_signaling_codes
ENUMERATED | 1 | 2034 | flag_assignment
ENUMERATED | 1 | 2035 | operating_mode_code
ENUMERATED | 1 | 2036 | analog_output_numbers_code
ENUMERATED | 1 | 2037 | rosemount_model_code
ENUMERATED | 1 | 2038 | rosemount_analytical_model_code
ENUMERATED | 1 | 2039 | kayray_model_code
ENUMERATED | 1 | 2040 | micro_motion_model_code
BIT_ENUMERATED | 1 | 4021 | xmtr_specific_status_0
BIT_ENUMERATED | 1 | 4022 | xmtr_specific_status_1
BIT_ENUMERATED | 1 | 4023 | xmtr_specific_status_2
BIT_ENUMERATED | 1 | 4024 | xmtr_specific_status_3
ENUMERATED | 1 | 4093 | burst_command_number
ENUMERATED | 1 | 4095 | burst_mode_select
ENUMERATED | 1 | 5020 | meter_installation
ENUMERATED | 1 | 16384 | digital_units
ENUMERATED | 1 | 16385 | sensor_type
ENUMERATED | 1 | 16391 | analog_output_transfer_function
FLOAT | 4 | 16392 | ma_analog_output_1_value
ENUMERATED | 1 | 16393 | ma_analog_output_1_alarm_select
FLOAT | 4 | 16394 | differential_measurement_digital_value
FLOAT | 4 | 16395 | differential_measurement_percent_range
FLOAT | 4 | 16396 | differential_measurement_upper_range_value
FLOAT | 4 | 16397 | differential_measurement_lower_range_value
FLOAT | 4 | 16398 | differential_measurement_damping_value
UNSIGNED | 3 | 16399 | sensor1_serial_number
FLOAT | 4 | 16400 | differential_measurement_upper_sensor_limit
FLOAT | 4 | 16401 | differential_measurement_lower_sensor_limit
FLOAT | 4 | 16402 | differential_measurement_minimum_span
ENUMERATED | 1 | 16403 | DEVICE_MODE
ENUMERATED | 1 | 16404 | number_wires
ENUMERATED | 1 | 16405 | electronics_temperature_digital_units
FLOAT | 4 | 16406 | electronics_temperature_digital_value
UNSIGNED | 3 | 16407 | electronics_temperature_serial_number
FLOAT | 4 | 16408 | electronics_temperature_upper_sensor_limit
FLOAT | 4 | 16409 | electronics_temperature_lower_sensor_limit
FLOAT | 4 | 16410 | electronics_temperature_damping_value
ENUMERATED | 1 | 16411 | sensor1_digital_units
FLOAT | 4 | 16412 | sensor1_measurement_digital_value
FLOAT | 4 | 16413 | sensor1_damping_value
FLOAT | 4 | 16414 | sensor1_upper_sensor_limit
FLOAT | 4 | 16415 | sensor1_lower_sensor_limit
ENUMERATED | 1 | 16416 | sensor2_digital_units
FLOAT | 4 | 16417 | sensor2_measurement_digital_value
UNSIGNED | 3 | 16418 | sensor2_serial_number
FLOAT | 4 | 16419 | sensor2_upper_sensor_limit
FLOAT | 4 | 16420 | sensor2_lower_sensor_limit
FLOAT | 4 | 16421 | sensor2_damping_value
UNSIGNED | 1 | 16423 | device_code
ENUMERATED | 1 | 16424 | lin_mode
ENUMERATED | 1 | 16427 | cal_locat
ENUMERATED | 1 | 16428 | cal_point_units
FLOAT | 4 | 16429 | upper_cal_point_limit
FLOAT | 4 | 16430 | lower_cal_point_limit
FLOAT | 4 | 16432 | cal_point
ENUMERATED | 1 | 16436 | CONTROLLER_TYPE
ENUMERATED | 1 | 16437 | POWER_UP_MODE
ENUMERATED | 1 | 16438 | CONTROLLER_ACTION
ENUMERATED | 1 | 16443 | unit_code
FLOAT | 4 | 16444 | PROCESS_VARIABLE | 83.45
FLOAT | 4 | 16445 | SETPOINT
FLOAT | 4 | 16446 | MANIPULATED_VARIABLE
ENUMERATED | 1 | 16447 | SETPOINT_TRACKING_MODE
ENUMERATED | 1 | 16448 | pid_mode
FLOAT | 4 | 16449 | ERROR_PERCENT_RANGE
FLOAT | 4 | 16452 | PROPORTIONAL_GAIN
FLOAT | 4 | 16453 | INTEGRAL_TIME
FLOAT | 4 | 16454 | DERIVATIVE_TIME
FLOAT | 4 | 16463 | MV_HIGH_LIMIT
FLOAT | 4 | 16464 | MV_LOW_LIMIT
FLOAT | 4 | 16465 | MV_ROC_LIMIT
FLOAT | 4 | 16468 | POWER_UP_SETPOINT_PERCENT_RANGE
FLOAT | 4 | 16469 | POWER_UP_OUTPUT
FLOAT | 4 | 16472 | set_point_time
ENUMERATED | 1 | 16473 | set_point_generator_mode
ENUMERATED | 1 | 16474 | set_point_time_generator_mode
INDEX | 1 | 16479 | coordinate_index
INTEGER | 1 | 16482 | table_points
UNSIGNED | 1 | 16485 | range_units
FLOAT | 4 | 16486 | upper_range_value
FLOAT | 4 | 16487 | lower_range_value
ENUMERATED | 1 | 16489 | alarm_0_action
ENUMERATED | 1 | 16490 | alarm_1_action
ENUMERATED | 1 | 16491 | alarm_2_action
FLOAT | 4 | 16492 | alarm_1_value
FLOAT | 4 | 16493 | alarm_2_value
ENUMERATED | 1 | 16494 | alarm_0_status
ENUMERATED | 1 | 16495 | alarm_1_status
ENUMERATED | 1 | 16496 | alarm_2_status
ENUMERATED | 1 | 16497 | alarm_0_acknowledge
ENUMERATED | 1 | 16498 | alarm_1_acknowledge
ENUMERATED | 1 | 16499 | alarm_2_acknowledge
ENUMERATED | 1 | 16505 | pv_display_code
ENUMERATED | 1 | 16506 | sv_display_code
INTEGER | 1 | 16509 | chg_cnt_range
INTEGER | 1 | 16510 | chg_cnt_function
INTEGER | 1 | 16511 | chg_cnt_trim_4
INTEGER | 1 | 16512 | chg_cnt_trim_20
INTEGER | 1 | 16513 | chg_cnt_trim
INTEGER | 1 | 16514 | chg_cnt_burnout
INTEGER | 1 | 16515 | chg_cnt_sensor
INTEGER | 1 | 16516 | chg_cnt_op_mode
INTEGER | 1 | 16517 | chg_cnt_local_adjust
INTEGER | 1 | 16518 | chg_cnt_com
INTEGER | 1 | 16519 | chg_cnt_multidrop
INTEGER | 1 | 16520 | chg_cnt_password
ENUMERATED | 1 | 16523 | communication_write_protection_mode
ENUMERATED | 1 | 16524 | local_adjust_protection_mode
ENUMERATED | 1 | 16527 | local_adjust_mode
ASCII | 6 | 16529 | pswd1
ASCII | 6 | 16530 | pswd2
ASCII | 6 | 16531 | pswd3
ASCII | 6 | 16532 | pswd4
UNSIGNED | 1 | 16534 | level_password
ASCII | 6 | 16535 | pswd
ASCII | 21 | 16537 | smar_order_code
ASCII | 1 | 16540 | first_character
ASCII | 1 | 16541 | second_character
ASCII | 1 | 16542 | third_character
ASCII | 1 | 16543 | fourth_character
ASCII | 1 | 16544 | fifth_character
FLOAT | 4 | 16547 | special_sensor_upper_range_limit
FLOAT | 4 | 16548 | special_sensor_lower_range_limit
FLOAT | 4 | 16549 | special_sensor_minimum_span
FLOAT | 4 | 16550 | special_sensor_high_limit
FLOAT | 4 | 16551 | special_sensor_low_limit
ENUMERATED | 1 | 16554 | input_unit_code
FLOAT | 4 | 16555 | special_sensor_ohms_mv_upper_limit
FLOAT | 4 | 16556 | special_sensor_ohms_mv_lower_limit
ENUMERATED | 1 | 16557 | special_sensor_gain
ENUMERATED | 1 | 16558 | special_sensor_connection
UNSIGNED | 1 | 16562 | conf_level_menu_1
UNSIGNED | 1 | 16563 | conf_level_menu_2
UNSIGNED | 1 | 16564 | conf_level_menu_3
UNSIGNED | 1 | 16565 | conf_level_menu_4
UNSIGNED | 1 | 16566 | conf_level_menu_5
UNSIGNED | 1 | 16567 | conf_level_menu_6
UNSIGNED | 1 | 16568 | conf_level_menu_7
UNSIGNED | 1 | 16569 | conf_level_menu_8
FLOAT | 4 | 16572 | output_variable
ENUMERATED | 1 | 16575 | mv_special_cold_junction
FLOAT | 4 | 16578 | not_used_1
FLOAT | 4 | 16579 | not_used_2
FLOAT | 4 | 16580 | mv_ohms
INTEGER | 1 | 16581 | not_used_3
ENUMERATED | 1 | 16582 | cal_point_limits_unit
FLOAT | 4 | 16583 | upper_cal_point_value
FLOAT | 4 | 16584 | lower_cal_point_value
ENUMERATED | 1 | 16585 | CONTROLLER_MODE
ENUMERATED | 1 | 16586 | fail_safe_mode
ENUMERATED | 1 | 16587 | sensor_range
FLOAT | 4 | 16588 | table_coordinate_0
FLOAT | 4 | 16589 | table_coordinate_1
FLOAT | 4 | 16590 | table_coordinate_2
FLOAT | 4 | 16591 | table_coordinate_3
FLOAT | 4 | 16592 | table_coordinate_4
FLOAT | 4 | 16593 | table_coordinate_5
FLOAT | 4 | 16594 | table_coordinate_6
FLOAT | 4 | 16595 | table_coordinate_7
FLOAT | 4 | 16596 | table_coordinate_8
FLOAT | 4 | 16597 | table_coordinate_9
FLOAT | 4 | 16598 | table_coordinate_10
FLOAT | 4 | 16599 | table_coordinate_11
FLOAT | 4 | 16600 | table_coordinate_12
FLOAT | 4 | 16601 | table_coordinate_13
FLOAT | 4 | 16602 | table_coordinate_14
FLOAT | 4 | 16603 | table_coordinate_15
FLOAT | 4 | 16604 | table_coordinate_16
FLOAT | 4 | 16605 | table_coordinate_17
FLOAT | 4 | 16606 | table_coordinate_18
FLOAT | 4 | 16607 | table_coordinate_19
FLOAT | 4 | 16608 | table_coordinate_20
FLOAT | 4 | 16609 | table_coordinate_21
FLOAT | 4 | 16610 | table_coordinate_22
FLOAT | 4 | 16611 | table_coordinate_23
FLOAT | 4 | 16612 | table_coordinate_24
FLOAT | 4 | 16613 | table_coordinate_25
FLOAT | 4 | 16614 | table_coordinate_26
FLOAT | 4 | 16615 | table_coordinate_27
FLOAT | 4 | 16616 | table_coordinate_28
FLOAT | 4 | 16617 | table_coordinate_29
FLOAT | 4 | 16618 | table_coordinate_30
FLOAT | 4 | 16619 | table_coordinate_31

## hrtFrame
Hart Short Frame |  |  |  | Hart Long Frame Example
Byte | Formato | Valor | Descrição | Byte | Formato | Valor | Descrição
- |  | FF FF FF FF | PREAMBLE | - |  | FF FF FF FF | PREAMBLE
0 |  | 06 ou 02 | DELIMITER | 0 |  | 82 ou 86 | DELIMITER
1 |  | 80 | ADDRESS | 1 |  | BE | MANUFACTERID
2 |  | 00 | COMMAND | 2 |  | 02 | DEVICETYPE
3 | 14 | 0E | NBBody | 3 |  | 00 | ADDRESS
4 | 1 | 00 | Body | 4 |  | 1E | ADDRESS
5 | 2 | 40 |  | 5 |  | 66 | ADDRESS
6 | 3 | FE |  | 6 |  | 00 | COMMAND
7 | 4 | 3E |  | 7 | 14 | 0E | NBBody
8 | 5 | 02 |  | 8 | 1 | 00 | Body
9 | 6 | 05 |  | 9 | 2 | 40
10 | 7 | 05 |  | 10 | 3 | FE
11 | 8 | 04 |  | 11 | 4 | 3E
12 | 9 | 30 |  | 12 | 5 | 02
13 | 10 | 01 |  | 13 | 6 | 05
14 | 11 | 00 |  | 14 | 7 | 05
15 | 12 | 00 |  | 15 | 8 | 04
16 | 13 | 1E |  | 16 | 9 | 30
17 | 14 | 66 |  | 17 | 10 | 01
18 |  | 47 | CheckSum | 18 | 11 | 00
|  |  |  | 19 | 12 | 00
|  |  |  | 20 | 13 | 1E
|  |  |  | 21 | 14 | 66
|  |  |  | 22 |  | 47 | CheckSum

## hrtCmd0
Identity Command |  |  |  |  | Identity Command
Comando 0 - Ver 5.2 Short Frame |  |  |  |  | Comando 0 - Ver 5.2 Long Frame
Byte | Formato | Valor | Descrição |  | Byte | Formato | Valor | Descrição
- |  | FF FF FF FF | PREAMBLE |  | - |  | FF FF FF FF | PREAMBLE
0 |  | 06 | DELIMITER (Short Frame) |  | 0 |  | 86 | DELIMITER (Long Frame)
1 |  | 80 | ADDRESS |  | 1 |  | BE ou 3E | MANUFACTERID (Last bit 1-Master 2-Slave)
2 |  | 00 | COMMAND |  | 2 |  | 02 | DEVICETYPE
3 | 14 | 0E | NBBody |  | 3 |  | 00 | DEVICE ID 1
4 | 1 | 00 | Body | Error Code | 4 |  | 1E | DEVICE ID 2
5 | 2 | 40 |  |  | 5 |  | 66 | DEVICE ID 3
6 | 3 | FE |  | Device Type Code for Expansion; "254" | 6 |  | 00 | COMMAND
7 | 4 | 3E |  | Manufacturer Identification Code | 7 | 14 | 0E | NBBody
8 | 5 | 02 |  | Manufacturer's Device Type Code | 8 | 1 | 00 | Body | Error Code
9 | 6 | 05 |  | Minimum number of Preambles required | 9 | 2 | 40
10 | 7 | 05 |  | HART Protocol Major Revision | 10 | 3 | FE |  | Device Type Code for Expansion; "254"
11 | 8 | 04 |  | Revision Level of the Universal Command | 11 | 4 | BE ou 3E |  | MANUFACTERID (Last bit 1-Master 2-Slave)
12 | 9 | 30 |  | Revision Level of the Transmitter-Specific Document | 12 | 5 | 02 |  | DEVICETYPE
13 | 10 | 01 |  | Hardware Revision Level of the electronics | 13 | 6 | 05 |  | Minimum number of Preambles required
14 | 11 | 00 |  | Flags Assignments | 14 | 7 | 05 |  | HART Protocol Major Revision
15 | 12 | 00 |  | DEVICE ID 1 | 15 | 8 | 04 |  | Revision Level of the Universal Command
16 | 13 | 1E |  | DEVICE ID 2 | 16 | 9 | 30 |  | Revision Level of the Transmitter-Specific Document
17 | 14 | 66 |  | DEVICE ID 3 | 17 | 10 | 01 |  | Hardware Revision Level of the electronics
18 |  | 47 | CheckSum |  | 18 | 11 | 00 |  | Flags Assignments
[5 empty] | 19 | 12 | 00 |  | DEVICE ID 1
[5 empty] | 20 | 13 | 1E |  | DEVICE ID 2
[5 empty] | 21 | 14 | 66 |  | DEVICE ID 3
[5 empty] | 22 |  | 83 | CheckSum

## hrtCmd1
Read Primary Variable
Comando 1 - Ver 5.2 Long Frame
Byte | Formato | Valor | Descrição
- |  | FF FF FF FF | PREAMBLE
0 |  | 86 | DELIMITER (Long Frame)
1 |  | BE ou 3E | MANUFACTERID (Last bit 1-Master 2-Slave) |  | Valor Real |  | 1.4862 |  |  |  | 5.8775e-39
2 |  | 02 | DEVICETYPE |  | S | Bit Last | 0 | 1 |  |  | 0
3 |  | 00 | DEVICE ID 1 |  | E | 8 Bits | 127 | 1 |  | 0 | 5.8775e-39
4 |  | 1E | DEVICE ID 2 |  | F | 23 Bits | 0.48616 | 1.4862 |  |  | 0
5 |  | 66 | DEVICE ID 3 |  |  |  | 01111100011101010000000 | 00000100 | 4 |  | 00000000000000000000000
6 |  | 01 | COMMAND |  |  | 1 | 0 |  |  | 1 | 0
7 | 7 | 07 | NBBody |  |  | 2 | 0.25 |  |  | 2 | 0
8 | 1 | 00 | Body | Error Code |  | 3 | 0.125 |  |  | 3 | 0
9 | 2 | 00 |  | Reserved |  | 4 | 0.0625 |  |  | 4 | 0
10 | 3 | 20 |  | Primary Variable Units |  | 5 | 0.03125 |  |  | 5 | 0
11 | 4 | 3F |  | Primary Variable 1 |  | 6 | 0.015625 |  |  | 6 | 0
12 | 5 | BE |  | Primary Variable 2 |  | 7 | 0 |  |  | 7 | 0
13 | 6 | 3A |  | Primary Variable 3 |  | 8 | 0 |  |  | 8 | 0
14 | 7 | 80 |  | Primary Variable 4 |  | 9 | 0 |  |  | 9 | 0
15 |  | XX | CheckSum |  |  | 10 | 0.00097656 |  |  | 10 | 0
[6 empty] | 11 | 0.00048828 |  |  | 11 | 0
[6 empty] | 12 | 0.00024414 |  |  | 12 | 0
[6 empty] | 13 | 0 |  |  | 13 | 0
[6 empty] | 14 | 6.1035e-05 |  |  | 14 | 0
[6 empty] | 15 | 0 |  |  | 15 | 0
[6 empty] | 16 | 1.5259e-05 |  |  | 16 | 0
[6 empty] | 17 | 0 |  |  | 17 | 0
[6 empty] | 18 | 0 |  |  | 18 | 0
[6 empty] | 19 | 0 |  |  | 19 | 0
[6 empty] | 20 | 0 |  |  | 20 | 0
[6 empty] | 21 | 0 |  |  | 21 | 0
[6 empty] | 22 | 0 |  |  | 22 | 0
[6 empty] | 23 | 0 |  |  | 23 | 0

## hrtCmd2
Read Loop Current And Percent Of Range
Comando 2 - Ver 5.2 Long Frame
Byte | Formato | Valor | Descrição
- |  | FF FF FF FF | PREAMBLE
0 |  | 86 | DELIMITER (Long Frame)
1 |  | BE ou 3E | MANUFACTERID (Last bit 1-Master 2-Slave)
2 |  | 02 | DEVICETYPE |  |  | Valor Real |  | 1.0151e-20
3 |  | 00 | DEVICE ID 1 |  |  | S | Bit Last | 0
4 |  | 1E | DEVICE ID 2 |  |  | E | 8 Bits | 60
5 |  | 66 | DEVICE ID 3 |  |  | F | 23 Bits | 0.49802
6 |  | 01 | COMMAND |  |  |  |  | 01111111011111100100000
7 | 10 | 0A | NBBody |  |  |  | 1 | 0
8 | 1 | 00 | Body | Error Code |  |  | 2 | 0.25
9 | 2 | 00 |  | Primary Variable 1 | Loop Current (milli-amperes) |  | 3 | 0.125
10 | 3 | 40 |  | Primary Variable 2 |  |  | 4 | 0.0625
11 | 4 | 87 |  | Primary Variable 3 |  |  | 5 | 0.03125
12 | 5 | A5 |  | Primary Variable 4 |  |  | 6 | 0.015625
13 | 6 | 1E |  | Primary Variable 1 | Percent of Range (percent) |  | 7 | 0.0078125
14 | 7 | 3F |  | Primary Variable 2 |  |  | 8 | 0.0039062
15 | 8 | BF |  | Primary Variable 3 |  |  | 9 | 0
16 | 9 | 20 |  | Primary Variable 4 |  |  | 10 | 0.00097656
20 |  | 00 | CheckSum |  |  |  | 11 | 0.00048828
[7 empty] | 12 | 0.00024414
[7 empty] | 13 | 0.00012207
[7 empty] | 14 | 6.1035e-05
[7 empty] | 15 | 3.0518e-05
[7 empty] | 16 | 0
[7 empty] | 17 | 0
[7 empty] | 18 | 3.8147e-06
[7 empty] | 19 | 0
[7 empty] | 20 | 0
[7 empty] | 21 | 0
[7 empty] | 22 | 0
[7 empty] | 23 | 0

## hrtCmd18
hrtCmd